## Weather File Station
Fort.Nelson-Northern.Rockies.Rgnl.AP.719450 | Past (TMY) | 2020s Future |  | 2020s Change |  | 2050s Future |  | 2050s Change |  | 2080s Future |  | 2080s Change
|  | Average | 10th%-90th% | Average | 10th%-90th% | Average | 10th%-90th% | Average | 10th%-90th% | Average | 10th%-90th% | Average | 10th%-90th%
HDD (Degree Days) | 6694 | 6370 | (6217 to 6470) | -324 | (-477 to -224) | 5804 | (5310 to 6022) | -890 | (-1384 to -672) | 5141 | (4561 to 5531) | -1553 | (-2133 to -1163)
TNN (°C) | -41.3 | -39.9 | (-41.4 to -38.8) | 1.4 | (-0.1 to 2.5) | -37.4 | (-39.2 to -34.5) | 3.9 | (2.1 to 6.8) | -34.2 | (-36.3 to -31.9) | 7.1 | (5 to 9.4)
Heating 99.0% (°C) | -32.4 | -31.3 | (-32 to -30.9) | 1.1 | (0.4 to 1.5) | -29.2 | (-30.6 to -28.1) | 3.2 | (1.8 to 4.3) | -26.2 | (-27.7 to -24.6) | 6.2 | (4.7 to 7.8)
Heating 97.5% (°C) | -27.3 | -26.2 | (-26.7 to -25.8) | 1.1 | (0.6 to 1.5) | -24.1 | (-25.6 to -22.9) | 3.2 | (1.7 to 4.4) | -21.4 | (-23.2 to -19.7) | 5.9 | (4.1 to 7.6)
Heating (Wetbulb) 99.0% (°C) | -33.8 | -32.7 | (-33.4 to -32.3) | 1.1 | (0.4 to 1.5) | -30.6 | (-32 to -29.5) | 3.2 | (1.8 to 4.3) | -27.6 | (-29.1 to -26) | 6.2 | (4.7 to 7.8)
Heating (Wetbulb) 97.5% (°C) | -28.7 | -27.6 | (-28 to -27.2) | 1.1 | (0.7 to 1.5) | -25.5 | (-27 to -24.3) | 3.2 | (1.7 to 4.4) | -22.8 | (-24.6 to -21.1) | 5.9 | (4.1 to 7.6)
CDD (Degree Days) | 30 | 52 | (41 to 67) | 22 | (11 to 37) | 130 | (77 to 189) | 100 | (47 to 159) | 284 | (135 to 484) | 254 | (105 to 454)
CDD10 (Degree Days) | 610 | 695 | (658 to 750) | 85 | (48 to 140) | 916 | (790 to 1054) | 306 | (180 to 444) | 1211 | (953 to 1502) | 601 | (343 to 892)
TXX (°C) | 29.5 | 30.1 | (29.3 to 31) | 0.6 | (-0.2 to 1.5) | 32.2 | (30.5 to 33.3) | 2.7 | (1 to 3.8) | 34.7 | (32.1 to 37.5) | 5.2 | (2.6 to 8)
Cooling 2.5% (°C) | 23.3 | 23.9 | (23.4 to 24.6) | 0.6 | (0.1 to 1.3) | 25.8 | (24.6 to 27) | 2.5 | (1.3 to 3.7) | 28.1 | (25.7 to 30.7) | 4.8 | (2.4 to 7.4)
Cooling (Wetbulb) 2.5% (°C) | 21.1 | 21.7 | (21.2 to 22.2) | 0.6 | (0.1 to 1.1) | 23.5 | (22.3 to 24.6) | 2.4 | (1.2 to 3.5) | 25.6 | (23.4 to 28) | 4.5 | (2.3 to 6.9)
Data Description
This tab summarizes the data from the
Fort.Nelson-Northern.Rockies.Rgnl.AP.719450 CWEC2016 Weather File
A description of each variable can be seen by hovering over the variable name in
Column A. The 'Past (TMY)' column summarizes data from the CWEC2016 weather file
while the remaining columns summarize future-shifted values. More details can be
found in the 'About This File' tab.
Note on B1: Variables calculated from the CWEC2016 TMY file
Note on C1: Variables calculated from the morphed TMY file for the 2020s
Note on E1: Differences in the variables between 2020s morphed TMY file and the CWEC2016 TMY File
Note on G1: Variables calculated from the morphed TMY file for the 2050s
Note on I1: Differences in the variables between 2050s morphed TMY file and the CWEC2016 TMY File
Note on K1: Variables calculated from the morphed TMY file for the 2080s
Note on M1: Differences in the variables between 2080s morphed TMY file and the CWEC2016 TMY File
Note on C2: Average of the 10 model ensemble of future scenarios for the 2020s
Note on D2: Range of the 10 model ensemble of future scenarios for the 2020s (10th and 90th percentiles of the ensemble are shown)
Note on E2: Average of the 10 model ensemble of future scenarios for the 2020s
Note on F2: Range of the 10 model ensemble of future scenarios for the 2020s (10th and 90th percentiles of the ensemble are shown)
Note on G2: Average of the 10 model ensemble of future scenarios for the 2050s
Note on H2: Range of the 10 model ensemble of future scenarios for the 2050s (10th and 90th percentiles of the ensemble are shown)
Note on I2: Average of the 10 model ensemble of future scenarios for the 2050s
Note on J2: Range of the 10 model ensemble of future scenarios for the 2050s (10th and 90th percentiles of the ensemble are shown)
Note on K2: Average of the 10 model ensemble of future scenarios for the 2080s
Note on L2: Range of the 10 model ensemble of future scenarios for the 2080s (10th and 90th percentiles of the ensemble are shown)
Note on M2: Average of the 10 model ensemble of future scenarios for the 2080s
Note on N2: Range of the 10 model ensemble of future scenarios for the 2080s (10th and 90th percentiles of the ensemble are shown)
Note on A3: HDD Heating Degree Days (Threshold: 18°C)
Note on A4: TNN Average seasonal and annual minimum of daily minimum temperature
Note on A5: Tasmin 1.0%ile Cold Month Design Temperature 1.0%ile
Note on A6: Tasmin 2.5%ile Cold Month Design Temperature 2.5%ile
Note on A7: Wetbulb Temperature 1.0%ile Cold Month Wetbulb Temperature 1.0%ile
Note on A8: Wetbulb Temperature 2.5%ile Cold Month Wetbulb Temperature 2.5%ile
Note on A9: CDD Cooling Degree Days (Threshold: 18°C)
Note on A10: CDD10 Cooling Degree Days (Threshold: 10°C)
Note on A11: TXX Average seasonal and annual maximum of daily maximum temperature
Note on A12: Tasmax 97.5%ile Warm Month Design Temperature 97.5%ile
Note on A13: Wetbulb Temperature 97.5%ile Warm Month Wetbulb Temperature 97.5%ile

## Temperature Climatologies
Fort_Nelson-Northern_Rockies_Rgnl_AP | Past (TMY) | TMY Year | BCCAQv2 Past | BCCAQv2 Past | 2020s Future |  | 2020s Change |  | 2050s Future |  | 2050s Change |  | 2080s Future |  | 2080s Change
|  |  | (1971-2000) | (1998-2014) | Average | 10th%-90th% | Average | 10th%-90th% | Average | 10th%-90th% | Average | 10th%-90th% | Average | 10th%-90th% | Average | 10th%-90th%
January Tmean (°C) | -18.9 | 2011 | -22 | -20.6 | -17.6 | (-18.1 to -16.8) | 1.3 | (0.7 to 2.1) | -15.2 | (-17.1 to -12.8) | 3.6 | (1.8 to 6.1) | -12.5 | (-14.7 to -10.3) | 6.3 | (4.2 to 8.6)
February Tmean (°C) | -13.7 | 2001 | -15.6 | -14.8 | -12.5 | (-13.5 to -11.7) | 1.1 | (0.1 to 1.9) | -11 | (-12.6 to -9.3) | 2.6 | (1 to 4.3) | -8.3 | (-10.1 to -4.6) | 5.4 | (3.6 to 9.1)
March Tmean (°C) | -8.7 | 2012 | -8.7 | -7.9 | -7.5 | (-8.6 to -6.4) | 1.2 | (0.1 to 2.3) | -5.8 | (-7.1 to -4.3) | 3 | (1.6 to 4.4) | -3.8 | (-5.2 to -1.5) | 4.9 | (3.6 to 7.2)
April Tmean (°C) | 3 | 2012 | 2 | 2.9 | 4 | (3 to 5) | 1 | (0 to 2) | 5 | (4 to 6) | 2 | (1 to 3) | 7 | (6 to 8) | 4 | (3 to 5)
May Tmean (°C) | 9.7 | 2014 | 9.5 | 10 | 10.4 | (10 to 10.8) | 0.7 | (0.3 to 1.1) | 11.7 | (11 to 12.3) | 2 | (1.3 to 2.6) | 13.5 | (12.3 to 14.9) | 3.8 | (2.6 to 5.2)
June Tmean (°C) | 14.8 | 2014 | 14.6 | 15.2 | 15.4 | (14.9 to 15.9) | 0.6 | (0.1 to 1.1) | 16.9 | (15.9 to 18.1) | 2.1 | (1.1 to 3.3) | 19 | (17.2 to 21.1) | 4.2 | (2.5 to 6.3)
July Tmean (°C) | 17 | 2000 | 16.6 | 17.4 | 17.8 | (17.5 to 18.1) | 0.8 | (0.5 to 1.2) | 19.6 | (18.5 to 20.9) | 2.7 | (1.5 to 4) | 21.8 | (19.6 to 24) | 4.8 | (2.6 to 7.1)
August Tmean (°C) | 14.7 | 2003 | 14.8 | 15.7 | 15.4 | (15 to 15.8) | 0.7 | (0.3 to 1.1) | 17.3 | (16.2 to 18.4) | 2.6 | (1.5 to 3.7) | 19.7 | (17.9 to 21.6) | 5 | (3.2 to 6.9)
September Tmean (°C) | 8.5 | 2003 | 9 | 9.6 | 9.4 | (8.8 to 9.7) | 0.9 | (0.4 to 1.3) | 11 | (9.8 to 12.2) | 2.5 | (1.3 to 3.7) | 13.2 | (11.3 to 15.3) | 4.7 | (2.8 to 6.8)
October Tmean (°C) | 0.9 | 2002 | 0.8 | 1.4 | 1.7 | (1.2 to 2.3) | 0.9 | (0.3 to 1.4) | 3.5 | (2.2 to 5) | 2.6 | (1.3 to 4.1) | 5.1 | (3.9 to 6.4) | 4.2 | (3 to 5.5)
November Tmean (°C) | -11.9 | 1999 | -11.9 | -11.2 | -10.7 | (-11.5 to -9.7) | 1.3 | (0.4 to 2.2) | -8.7 | (-10.2 to -6.8) | 3.3 | (1.7 to 5.2) | -6.3 | (-8.8 to -4.5) | 5.7 | (3.2 to 7.4)
December Tmean (°C) | -19.3 | 2004 | -19.2 | -18 | -18.1 | (-18.7 to -17.7) | 1.2 | (0.6 to 1.6) | -15.9 | (-17.6 to -15.1) | 3.4 | (1.7 to 4.2) | -12.9 | (-14.6 to -11.6) | 6.4 | (4.7 to 7.7)
Winter Tmean (°C) | -17.4 | NA | -19 | -17.8 | -16.2 | (-16.6 to -15.6) | 1.2 | (0.8 to 1.7) | -14.2 | (-15.8 to -12.9) | 3.2 | (1.6 to 4.5) | -11.3 | (-13 to -9.4) | 6.1 | (4.4 to 8)
Spring Tmean (°C) | 1 | NA | 0.9 | 1.7 | 2 | (2 to 3) | 1 | (0 to 2) | 4 | (3 to 5) | 2 | (2 to 3) | 6 | (5 to 7) | 4 | (3 to 6)
Summer Tmean (°C) | 15.5 | NA | 15.3 | 16.1 | 16.2 | (15.8 to 16.7) | 0.7 | (0.3 to 1.2) | 18 | (16.9 to 19.1) | 2.5 | (1.4 to 3.6) | 20.2 | (18.3 to 22.4) | 4.7 | (2.8 to 6.9)
Fall Tmean (°C) | -0.8 | NA | -0.7 | 0 | 0.2 | (-0.3 to 0.7) | 1 | (0.6 to 1.6) | 2 | (0.7 to 3.4) | 2.8 | (1.5 to 4.3) | 4 | (2.3 to 5.9) | 4.9 | (3.1 to 6.7)
Annual Tmean (°C) | -0.3 | NA | -0.8 | 0 | 0.7 | (0.4 to 1.1) | 0.9 | (0.7 to 1.4) | 2.5 | (1.8 to 4) | 2.7 | (2.1 to 4.2) | 4.7 | (3.2 to 6.8) | 4.9 | (3.4 to 7.1)
Plot Description
The plot to the left displays temperature climatologies
from the above table. The blue 'Past' lines correspond to
the 'Past (TMY)' column. The boxplots are computed from
the ensemble of future projections for the 2020s, 2050s,
and 2080s that is summarized in the 'Future' columns.
Note on B1: Mean temperatures calculated from the CWEC2016 TMY file
Note on C1: Mean temperatures calculated from the CWEC2016 TMY file
Note on D1: Mean temperatures calculated from the model scenario past
Note on E1: Mean temperatures calculated from the model scenario past
Note on F1: Mean temperatures calculated from the morphed TMY file for the 2020s
Note on H1: Differences in mean temperatures between 2020s morphed TMY file and the CWEC2016 TMY File
Note on J1: Mean temperatures calculated from the morphed TMY file for the 2050s
Note on L1: Differences in mean temperatures between 2050s morphed TMY file and the CWEC2016 TMY File
Note on N1: Mean temperatures calculated from the morphed TMY file for the 2080s
Note on P1: Differences in mean temperatures between 2080s morphed TMY file and the CWEC2016 TMY File
Note on F2: Average of the 10 model ensemble of future scenarios for the 2020s
Note on G2: Range of the 10 model ensemble of future scenarios for the 2020s (10th and 90th percentiles of the ensemble are shown)
Note on H2: Average of the 10 model ensemble of future scenarios for the 2020s
Note on I2: Range of the 10 model ensemble of future scenarios for the 2020s (10th and 90th percentiles of the ensemble are shown)
Note on J2: Average of the 10 model ensemble of future scenarios for the 2050s
Note on K2: Range of the 10 model ensemble of future scenarios for the 2050s (10th and 90th percentiles of the ensemble are shown)
Note on L2: Average of the 10 model ensemble of future scenarios for the 2050s
Note on M2: Range of the 10 model ensemble of future scenarios for the 2050s (10th and 90th percentiles of the ensemble are shown)
Note on N2: Average of the 10 model ensemble of future scenarios for the 2080s
Note on O2: Range of the 10 model ensemble of future scenarios for the 2080s (10th and 90th percentiles of the ensemble are shown)
Note on P2: Average of the 10 model ensemble of future scenarios for the 2080s
Note on Q2: Range of the 10 model ensemble of future scenarios for the 2080s (10th and 90th percentiles of the ensemble are shown)
Note on A3: January Average Temperature Monthly averaged daily average temperature
Note on A4: February Average Temperature Monthly averaged daily average temperature
Note on A5: March Average Temperature Monthly averaged daily average temperature
Note on A6: April Average Temperature Monthly averaged daily average temperature
Note on A7: May Average Temperature Monthly averaged daily average temperature
Note on A8: June Average Temperature Monthly averaged daily average temperature
Note on A9: July Average Temperature Monthly averaged daily average temperature
Note on A10: August Average Temperature Monthly averaged daily average temperature
Note on A11: September Average Temperature Monthly averaged daily average temperature
Note on A12: October Average Temperature Monthly averaged daily average temperature
Note on A13: November Average Temperature Monthly averaged daily average temperature
Note on A14: December Average Temperature Monthly averaged daily average temperature
Note on A15: Winter Average Temperature Seasonally averaged daily average temperature
Note on A16: Spring Average Temperature Seasonally averaged daily average temperature
Note on A17: Summer Average Temperature Seasonally averaged daily average temperature
Note on A18: Fall Average Temperature Seasonally averaged daily average temperature
Note on A19: Annual Average Temperature Annually averaged daily average temperature

## About This File
About This File
File Description
This file contains summary statistics for the
Fort.Nelson-Northern.Rockies.Rgnl.AP.719450CWEC2016 Weather File
Further about the variables in the rows can be seen by hovering over the row headings
(Column A) of each tab. This summary file for the past and future-shifted weather
files (Version 2.1) was downloaded from:
https://pacificclimate.org/data/weather-files
More information about each tab is provided in the descriptions below.
Methods and more information
These future-shifted weather files were created by applying morphing factors (Belcher,
et al., 2005) from an ensemble of 10 global climate models selected for Western Canada
(Cannon, 2015). Daily morphing factors (smoothed with a 21-day rolling mean) are
applied to the following variables:
dry bulb temperature, dewpoint temperature, relative humidity, surface pressure
Dry bulb temperature morphing factors are obtained from downscaled (BCCAQv2) climate
models (Cannon et al., 2015). Morphing factors for other variables are obtained from
GCMs interpolated to the BCCAQv2 resolution (about 10 km).
For a description of the TMY methodology see:
https://climate.onebuilding.org/papers
For the complete set of CWEC2016 files see:
https://climate.weather.gc.ca/prods_servs/engineering_e.html
For the more information on the 'morphing' procedure see:
www.pacificclimate.org/sites/default/files/Eketal_2018_Proceedings_22_Feb_2019.pdf
For a detailed description of BCCAQv2 see:
https://pacificclimate.org/data/statistically-downscaled-climate-scenarios
Weather File Station Tab
The 'Past (TMY)' column summarizes the data from
CAN_BC_Fort.Nelson-Northern.Rockies.Rgnl.AP.719450_CWEC2016.epw
while the remaining columns summarize future-shifted values (i.e. data from files:
2020s_CAN_BC_Fort.Nelson-Northern.Rockies.Rgnl.AP.719450_CWEC2016.epw
2050s_CAN_BC_Fort.Nelson-Northern.Rockies.Rgnl.AP.719450_CWEC2016.epw
2080s_CAN_BC_Fort.Nelson-Northern.Rockies.Rgnl.AP.719450_CWEC2016.epw).
The 2020s, 2050s, and 2080s columns summarize information averaged over the 30-year
period, based on the change according to the average, 10th percentile, and 90th
percentile from the 10-model ensemble. The percentiles are provided to encapsulate
the range of plausible future change under the RCP8.5 (high emissions) scenario.
Temperature Climatologies Tab
The temperature climatologies tab shows monthly, seasonal, and annual temperature
averages. Temperatures for the past are shown from both the TMY file and from the
gridded historical past (BCCAQv2) averaged over the years 1998-2014. This is the period
from which TMY months are chosen for the CWEC2016 files. Future changes in monthly,
seasonal and annual average temperatures from the ensemble of 10 BCCAQv2 downscaled
scenarios are also shown.
References
Belcher, S.E., Hacker, J. and Powell, D.S. (2005) Constructing design
weather data for future climates. Building Services Engineering Research and
Technology. 26. 10.1191/0143624405bt112oa.
Cannon, A.J.,Sobie, S.R., and Murdock, T.Q. (2015) Bias correction of GCM
precipitation by quantile mapping: How well do methods preserve changes in
quantiles and extremes? J. Clim., 28, pp. 6938-6959
Cannon,A.J. (2015) Selecting GCM scenarios that span the range of changes
in a multimodel ensemble: application to CMIP5 climate extremes indices
J. Clim. 28, pp. 1260-1267